Old Mill Road Storm Drain Inspection and Condition Notes

Brookhaven County Public Works | Inspection dates: 2026-04-08 to 2026-04-12 | Finalized: 2026-04-18

# 1. Inspection scope and use instruction

These inspection notes provide the current field condition basis for existing-pipe roughness and maintenance constraints. Where these notes conflict with the preliminary calculation workbook's generic Manning n values, use the condition-based values below for the existing-condition capacity check.

# 2. Pipe condition table

| Asset | Material | Observed condition | Sediment/debris | Joint condition | Existing-condition n | Engineering note |
| --- | --- | --- | --- | --- | --- | --- |
| P-1 | RCP | Minor staining, no barrel deformation | <5 percent area | tight joints | 0.013 | Use slightly aged RCP roughness. |
| P-2 | RCP | Moderate staining with offset joints at two locations | 8-12 percent area | minor offsets | 0.015 | Use condition roughness; generic 0.012 is not appropriate. |
| P-3 | RCP | Aged barrel with visible joint offset and sediment shelf | 12-18 percent area | offset joints | 0.015 | Use condition roughness; inspect after cleaning. |
| P-4 | CMP | Rust scaling, flattened corrugation peaks, debris at outlet | 10-15 percent area | not applicable | 0.024 | Use aged CMP roughness for existing condition. |
| OUT-1 arch | CMP arch | Rust, debris rack partially blocked, apron undermined | 20 percent inlet obstruction observed | not applicable | 0.024 | HDS-5 screening must note uncertain inlet blockage and tailwater. |

# 3. Node observations

| Node | Observation | Measured sediment depth | Public complaint link | Recommended treatment |
| --- | --- | --- | --- | --- |
| CB-1 | Grate clear during inspection; gutter depression holds shallow ponding after storm. | 0.05 ft | Several minor splash complaints | Regrade gutter lip only if full sag reconstruction proceeds. |
| MH-2 | No surcharge stain above crown; lateral flow from swale visible. | 0.10 ft | No direct complaints | Clean pipe inlet before construction. |
| MH-3 | Surcharge stain approximately 0.40 ft below rim. | 0.18 ft | Maintenance crew noted gurgling. | Use in HGL profile; confirm after P-3 cleaning. |
| CB-3 | Debris line on curb return and inlet throat; high-water mark 0.08 ft below gutter during April 9 event. | 0.25 ft | Primary complaint cluster | Hydraulic capacity improvement required. |
| OUT-1 | Tailwater mark at 212.34 ft; woody debris on upstream face. | 0.30 ft at inlet | Downstream resident reports yard flooding | Carry tailwater/debris uncertainty as open item. |

# 4. Maintenance and permitting notes

Routine pipe cleaning is allowed within the existing right-of-way.

In-channel work at Willow Branch requires permit readiness before construction authorization.

No recorded easement exists for work south of parcel 17-044; the county surveyor flagged this in the ROW review.

Sediment removal alone is not expected to resolve the 25-year sag flooding condition.